## Slide 1: From Copper to Optics for AI scale-up
Joyce Poon
Toronto Wireline Workshop | March 6, 2026
Views expressed are my own and do not represent those of my former employer or any other organization.

## Slide 2: Overview of an AI cluster
XPU
XPU
XPU
…
…
XPU
XPU
XPU
…
…
…
…
RACK
RACK
RAIL
…
RAIL
SPINE
…
SCALE-UP
Connections to next pod
SCALE-OUT
Notes: Traffic per rail of each compute tray is always one hop away from other compute trays in the same Scalable Unit. Traffic between different compute racks, or between different rails, traverses the spine layer.
https://docs.nvidia.com/dgx-superpod/reference-architecture-scalable-infrastructure-gb200/latest/network-fabrics.html

## Slide 3: Interconnects
Scale-up
  Between XPUs in a rack (distance: 2 - ~10 m)
  Protocols: NVLink, UALink, Scale-Up Ethernet
Scale-out
  Between racks and pods (distance: 100s m)
  Protocols: Ethernet, InfiniBand
    Interoperability
Important metrics
  Bandwidth density
  Power consumption
  Latency
https://docs.nvidia.com/dgx-superpod/reference-architecture-scalable-infrastructure-b200/latest/network-fabrics.html
Example: NVIDIA DGX SuperPod
Why bandwidth density matters…
Source: SemiAnalysis
Notes: https://docs.nvidia.com/dgx/dgxgb200-user-guide/hardware.html

## Slide 4: Power consumption
Example: NVIDIA GB200 NVL72
System (per rack)
  72 GPUs + 36 CPUs
  Power: ~130 kW
    Switches: 7 kW1, NVLink IO: 6-12 kW (assuming 10-20 pJ/bit)
    Scale-up IO is 5-10% of the total rack power
Scale-up connectivity (per direction)
  18 ports (NVLink 5) x 400 Gbps per GPU
  Throughput per GPU: 7.8 Tbps
  Lane rate: 224 Gb/s
Cabling
  1296 copper cables per rack
  5184 high-speed lanes (bi-dir)
Top of rack Ethernet switch
Power
10 Compute Trays
9 Switch Trays
(18 switches)
8 Compute Trays
Power
Cooling
https://developer.nvidia.com/blog/nvidia-gb200-nvl72-delivers-trillion-parameter-llm-training-and-real-time-inference/
Copper backplane
https://www.supermicro.com/en/products/system/gpu/48u/srs-gb200-nvl72
1 https://newsletter.semianalysis.com/p/gb200-hardware-architecture-and-component
🧱
Notes: https://docs.nvidia.com/dgx-superpod/reference-architecture-scalable-infrastructure-gb200/latest/_downloads/238ab33ee345a7241fc2f15eedc2ff6c/RA11338001-DSPGB200-ReferenceArch.pdf
https://newsletter.semianalysis.com/p/gb200-hardware-architecture-and-component

## Slide 5: Number of GPUs in a rack
NVIDIA
Chart: 
| 2025 | 2026 | 2027
GPUs per Rack | 72 | 144 | 576
8X

## Slide 6: Scale-up latency
Source: N. Nedovic (NVIDIA), ISSCC 2026
GPU → Switch → GPU: 260-700 ns
 | Item | Total Latency (ns)
1 | SerDes + DSP + Analog Front End | 50 – 100 ns
2 | Time of flight [2 to 10 meters] | 10 – 50 ns
3 | FEC | 50 – 100 ns
4 | Encryption | 0 – 50 ns
5 | Switch port-to-port | 100 – 200 ns
6 | Other | 50 – 200 ns
SWITCH ASIC
GPU
GPU
(1)
(2)
(1)+(3)
(2)
(5)
(1)
(1)+(3)

## Slide 7: Other architectures
Google Ironwood
Huawei Ascend 910C Cloud Matrix 384
48 lanes x 112G
Topology
  3D torus network with MEMS Optical Circuit Switch
  1:6 TPU:TPU connectivity
Scale
  Rack: 64 TPUs; Pod: 9216 TPUs
  # of lanes per rack: 64 x 48 x 2 directions = 6144
Interconnect
  4.8 Tbps per GPU (uni-dir)
  Copper
  112Gbps per lane
https://docs.cloud.google.com/tpu/docs/tpu7x
Scale-up Switches
Top of the rack switches
NPUs
NPUs
Topology
  2-Tier network
  All-to-all connections
Scale
  Rack: 32 NPUs; Pod: 384 NPUs
  # of lanes per rack: 32 x 28 x 2 directions = 1792
Interconnect
  2.8 Tbps per GPU (uni-dir)
  Linear pluggable optics
  112Gbps per lane (likely)
https://newsletter.semianalysis.com/p/huawei-ai-cloudmatrix-384-chinas-answer-to-nvidia-gb200-nvl72

## Slide 8: Comparison
 | Units | NVIDIA GB NVL72 | Google Ironwood | Huawei CloudMatrix 384 | NVIDIA VR NVL144 | NVIDIA VR NVL576
Number of GPUs per rack |  | 72 | 64 | 32 | 144 | 576
Scale-up technology |  | Copper | Copper | Linear Pluggable Optics | Copper | Copper?
Scale-up BW per GPU | Gbps (uni-dir) | 7200 | 4800 | 2800 | 7200 | 10400
Lane rate | Gbps | 224 | 112 | 112 (tbc) | 224 | 224 (bi-dir?)
Scale-up BW per rack | Tbps (bi-dir) | 1036 | 615 | 180 | 2080 | 12000
Power consumption per rack | kW | ~140 | - | 600 | 190-230 | 600
% Power for IO |  | 5-10% (est.) | - | - | ~10-20% (est.) | 20-40%??
As the number of GPUs per rack doubles per year, the scale-up bandwidth also grows.
Late 2026
Late 2027
Notes: NVIDIA 576 rack will also hit 600kW per rack
NVL144: 2080Tbps per rack x 10 pJ/b = 20.8 kW for IO
2080Tbps per rack x 20 pJ/b = 42 kW for IO

## Slide 9: Why not optics (yet)?
Example from Huawei
High power consumption
Optical transceiver failure rates: 6.3 per 1000
“Of the training interruptions caused by optical transceivers, 30% are due to contamination of the transceiver, and 70% are due to single-channel failures within the transceiver”
Source: Huawei whitepaper 2024
Top components causing compute-node failures
Optical transceivers
Other
Memory
Motherboard
Optical module failure mode distribution
Laser: 90.52%
Other: 3.02%
PCB: 0.6%
ODSP: 2.6%
Receiver:3.2%
Laser single-channel faults account for as high as 90%
1. Pre-training compute-network coordinated stress testing, identifying sub-healthy links early to resolve 70%+ of hidden risks before training
Compute
Network
2. During training, compute-network coordination with optical module channel damage-tolerance technology, mitigating 90% of optical module faults.

## Slide 10: Why optics?
Substrate
PCB
ASIC
OE
DSP
Substrate
PCB
ASIC
OE
Substrate
PCB
ASIC
OE
Substrate
PCB
ASIC
Interposer
OE
Pluggable Retimed Optics
Near-Package Optics
or Linear Pluggable Optics
Co-Packaged Optics
Optical Interposer
LR
LR/MR
XSR
ASIC
ASIC
ASIC
Energy efficiency
~10-15 pJ/b
~5-10 pJ/b
~3-5 pJ/b
Scale-out
Scale-Up
2026
1CloudMatrix: 7W per 400G LPO transceiver = 17.5pJ/b
ASIC
15-20 pJ/b
(2 fewer DSP in OE)
(2 fewer DSP in OE,
XSR vs. LR)
(2 fewer DSP in OE,
better signal integrity)

## Slide 11: CPO reliability
Example: Meta and Broadcom
Implications for scale-up
  1049k port device hours means
    1 Pod: [(18 ports x 72 GPU)GPU + (18 x 72)Switch ] x 8 racks = 50.6 hours
    16 Pods: 3 hours (ref: NVIDIA DGX Compute Fabric)
Promising, and continued improvement in link integrity desirable for large clusters
Broadcom Tomahawk 5 switches
(Each switch: 128 ports @ 400G per port)
S. Amiralizadeh et al., Co-packaged optics technology evaluation for hyperscale data center fabric switches, ECOC, 2025.

## Slide 12: CPO with advanced packaging
Example: TSMC Compact Universal Photonic Engine (COUPE)
Chip-on-Wafer-on-Substrate (CoWoS)
3D-stacked EIC on PIC
EIC: Electronic integrated circuit
PIC: Photonic integrated circuit
Observations
Si photonics leverages CMOS manufacturing & packaging
Compact transceivers (≲ 55 μm x 55 μm) simplifies 3D EIC-PIC integration
10 Tbps/mm ⇒ ~1.3 Tbps / fiber @ 127μm fiber pitch
Interface (e.g., UCIe-2.5D)
Density: 1-10 Tbps/mm
Figures from S. Hou (TSMC), OCP APAC Summit, 2025.

## Slide 13: VCSELs and microLEDs
Spatially wide-and-parallel links
10 Tbps/mm ⇒ 200 Gbps / 20 μm
Multi-core fiber and imaging fiber bundles
  Crosstalk between cores for λ ≳ 530 nm
  Multimode emission ⇒ coupling loss to single-mode fiber cores
  No fiber connectors
    Our attempt with core expansion: Govdeli et al., CLEO 2022
Fujikura FIGH-30-650S
Diameter: 650 μm
~30000 cores @ ~1 μm dia.
Inter-core spacing: ~ 3.3 μm
Fiber bundle facet
Azadeh et al., Optics Letters, 2022
Cores are not uniform in size and position
From my group’s neurotech research
Fujikura imaging fiber bundle
Custom multi-core fiber with Corning
10 single-mode cores
16 single-mode cores
Pitch: 16 um
Dia: 300 um
Pitch: 24 um
Dia: 300 um
10-core
250 m
16 core
5 m
Requires substantial technology & supply chain development!

## Slide 14: Silicon photonics
Mach-Zehnder Modulators & Lattice Filters
L = 2 – 3 mm
Mature technology
Large footprint, large DWDM circuits
Modulation EO BWs: up to ~90 GHz
2.8 mm
4.5 mm
16λ MUX/DEMUX
MZM
L = 30 – 50 um
GeSi Electroabsorption Modulators
imec
Bulk GeSi: operates near 1550 nm
Bandgap shift dλ/dT = 0.8 nm⋅K-1
Thermal stabilization to ~ 5 K
Heat EAM for broadband coverage
Use MZ lattice or ring filters for WDM
D. Feng et al. (Kotura), JSTQE, 2013.
EAM
Unless otherwise noted, images are from my research.
λ1, λ2, λ3…
λ1
λ2
λ3
λ16
…
λ1
D = 12 – 40 um
Microring Modulators
& Filters
Wavelength shift: dλ/dT = ~60 pm⋅K-1
  -10.5 GHz⋅K-1
Thermal stabilization to ~0.5 K
Highly compact serial MUX/DEMUX
MRM
200 um
Ring 1
λ1
Ring 2
λ2
Ring 3
λ3
Ring 4
λ4
MRM + MUX
λ1, λ2, λ3…
Coupled rings for filter shaping
λ1, λ2, λ3…
λ1
λ1
λ1
λ1

## Slide 15: 1.6 Tbps per fiber
Spectrally wide-and-parallel vs. High-speed serial
Option | Number of Wavelengths | Lane Rate (Gbps) | Modulation Format | Modulator
A | 32 | 50 | NRZ | MRM
B | 16 | 100 | PAM4 | MRM
C | 16 | 100 | NRZ | MRM
D | 8 | 200 | PAM4 | MRM, EAM*
E | 8 | 200 | NRZ | MRM, EAM*
F | 4 | 400 | PAM4 | MRM, EAM*, MZM*
*EAMs and MZMs need more laser fibers (one per wavelength) than MRMs, so the bandwidth density will be lower

## Slide 16: Optical link budget
Modulation Rate and Format | Input power : OMA (dB) | TDEC(Q) (dB)
MRM 50G NRZ | 2.5 | 0.5
MRM 100G NRZ | 6 | 1
MRM 100G PAM4 | 3.5 | 2
MRM 200G PAM4 | 6 | 3
EAM 100G NRZ | 5 | 1.5
EAM 100G PAM4 | 6 | 2
EAM 200G PAM4 | 7 | 3.5
2.5 dB
0.5 dB
2.5 dB
3 dB
2.5 dB
0.5 dB
32λ:1.5 dB
16λ: 1 dB
8λ: 0.5 dB
Modulation Rate & Format | RX OMA (dBm)
50G NRZ | -12
100G NRZ | -11
100G PAM4 | -10
200G PAM4 | -8
2 dB
Transmitter Penalty
Receiver Sensitivity

## Slide 17: Energy efficiency
Chart: Photonic IC + Laser (pJ/b)
| 1.5795585688119971 | 1.4264404343742076 | 1.214364350796509 | 1.5797130061774638 | 1.4361248021024651 | 1.9818995083657698 | 2.1111816339623468
pJ per bit | 2 | 2.4623 | 2.4623 | 3.0314 | 2.4623 | 2.4623 | 3.0314
6W | 0 | 3.75
8W | 0 | 4.375
10W | 0 | 5
12W | 0 | 5.625
PIC+Laser | Value per λ
MRM tuning | 20 mW
EAM tuning | 10 mW
λ-MUX (EAM) | 20 mW
λ-DEMUX | 20 mW
Laser WPE | 12%
Observations
Trade-off between optical power and electrical power
  Increase symbol rate ⇒ PIC pJ/bit decreases (amortization of DC dissipation) in exchange for laser and EIC+XSR pJ/bit (DSP)
Laser is 50-90% of the optical pJ/bit
  Reduce major losses and penalties: fiber couplers, modulator penalty
EIC + XSR | pJ/b
50G NRZ | 2
100G NRZ | 2.5
100G PAM4 | 2.5
200G PAM4 | 3.0

## Slide 18: Latency: a rough estimate
NRZ offers the lowest latency due to reduced/no FEC
Higher data rate ⇒ Lower latency
Time-of-flight is a large fraction of the latency
With today’s 200G-PAM4 technology, consider 100G NRZ for best energy efficiency and latency
Chart: Latency (ns)
| 100G PAM4 | 200G PAM4 | 50G NRZ | 100G NRZ
Fiber ToF | 25 | 25 | 25 | 25
TX Ser, Eq, AFE | 5 | 3 | 4.5 | 2.5
RX DeSer, DSP, CDR, AFE | 14.1569 | 8.5 | 16 | 9.6569
Lite FEC | 50 | 35.3553 | 0 | 0

## Slide 19: MRM WDM link examples
Single-wavelength per fiber MRM links
Ranovus: 100G PAM4 (ref)
Intel: 240Gbps (OFC 2022)
NVIDIA: 200Gbps (OFC 2026?)
Ayar Labs (OFC 2025)
16λ x 32G NRZ = 512 Gbps
NVIDIA Research (ISSCC 2026)
8λ x 32G NRZ = 256 Gbps
Lightmatter (OFC 2026)
16λ x 56G NRZ = 896 Gbps (bi-dir)
Intel (OFC & Hot Chips 2024)
8λ x 32G NRZ = 256 Gbps (integrated lasers)

## Slide 20
Lightmatter: 16λ x 112G PAM4

## Slide 21: DWDM laser source examples
Ayar Labs with Sivers
Monolithic InP DFB array
16λ x 200GHz
Scintil Photonics
Hybrid InP-on-Si
16λ x (100 or 200 GHz)
18 x 200 GHz
Lightmatter
Single-chip integrated
16λ x 200 GHz, 32 fiber output
100 mW per λ

## Slide 22: Toward 400-448G PAM4 per lane
Nyquist: 100-112GHz
Intrinsic Si PN junction bandwidth
  C = 0.5 to 1 pF/mm
  R = 1 - 2 Ohm·mm
  ⇒ 80 - 300 GHz ✅
Mach-Zehnder Modulators
BW of CPW electrodes is typically limited by RF loss
E.g., Segmented electrodes
Microring Modulators
Conventional MRM: challenging (Q ≲ 1000)
Coupling-modulated microring?
Aloe Semiconductor
180 Gbaud
Coupling modulation
W. Sacher et al., Optics Express, 2013.
Beyond Si: Thin film LiNbO3, EO polymers, BaTiO3, ferroelectric liquid crystals

## Slide 23: Summary
System requirements on scale-up networks
~104 Tbps-class interconnects per rack ➞ Supply chain
Bandwidth density, power consumption, latency, reliability
Limits of copper
Works today (up to 200G per lane)
Complexities are growing (rack power, cable management)
Co-packaged optics for 1.6 Tbps/fiber and beyond
WDM + moderately high (100+G) lane rate to achieve bandwidth density
NRZ for the lowest latency
Today’s limit: Microring based 16λ x 112G ➞1.6Tbps per fiber
400G-class transceivers are not fundamentally out of reach for Si photonics
Views expressed are my own and do not represent those of my former employer or any other organization.